## Sheet1
ITEM NO. | AREA | Room_number | Room_name | Temperature_Limit | Humidity_Low_Limit | Humidity_High_Limit | Pressure_Low_Limit | Pressure_High_Limit | Room_Pressure_Comparison
1 | Module 1 | 1-P032 | Airlock 1 | 25 | 35 | 30 | 10 | 20 | 1-P034
2 | Module 1 | 1-P033 | Changing Room | 25 |  |  | 10 | 20 | 1-P034
3 | Module 1 | 1-P034 | Buffer Area | 25 | 35 | 65 | 25 | 35 | 1-P034
4 | Module 1 | 1-P037 | Washing Room | 25 |  |  | 10 | 20 | 1-P051
5 | Module 1 | 1-P036 | Cleaned Equipment Storage | 25 | 35 | 65 | 40 | 50 | 1-P034
6 | Module 1 | 1-P035 | Janitor Room | 25 | 35 | 65 | 10 | 20 | 1-P034
7 | Module 1 | 1-P038 | Granulation Room | 25 | 35 | 50 | 10 | 20 | 1-P051
8 | Module 1 | 1-P039 | Binder Preparation Room | 25 | 35 | 65 | 10 | 20 | 1-P051
9 | Module 1 | 1-P040 | Mixing Room | 25 | 30 | 50 | 10 | 20 | 1-P051
10 | Module 1 | 1-P041 | Granule Storage | 25 | 35 | 55 | 10 | 20 | 1-P051
11 | Module 1 | 1-P042 | Tableting Room 1 | 25 | 30 | 50 | 10 | 20 | 1-P051
12 | Module 1 | 1-P043 | Tableting Room 2 | 25 | 30 | 50 | 10 | 20 | 1-P051
13 | Module 1 | 1-P044 | In Process Control Room | 25 | 35 | 65 | 10 | 20 | 1-P051
14 | Module 1 | 1-P045 | Core Tablet Storage | 25 | 35 | 55 | 10 | 20 | 1-P051
15 | Module 1 | 1-P046 | Coating Preparation Room | 25 | 30 | 50 | 10 | 20 | 1-P051
16 | Module 1 | 1-P047 | Coating Room 1 | 25 | 30 | 50 | 10 | 20 | 1-P051
17 | Module 1 | 1-P048 | Coating Room 2 | 25 | 30 | 50 | 10 | 20 | 1-P051
18 | Module 1 | 1-P049 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 1-P051
19 | Module 1 | 1-P051 | Corridor | 25 | 35 | 65 | 25 | 35 | 1-P051
20 | Module 1 | 1-P072 | Airlock 2 | 25 | 35 | 65 | 40 | 50 | 1-P051
21 | Module 1 | 1-P167 | Airlock | 25 | 35 | 65 | 25 | 35 | 1-P051
22 | Module 2 | 1-P052 | Corridor | 25 | 35 | 65 | 25 | 35 | 1-P052
23 | Module 2 | 1-P053 | Corridor | 25 | 35 | 65 | 25 | 35 | 1-P053
24 | Module 2 | 1-P054 | Airlock 1 | 25 | 35 | 65 | 10 | 20 | 1-P056
25 | Module 2 | 1-P055 | Changing Room | 25 |  |  | 10 | 20 | 1-P056
26 | Module 2 | 1-P056 | Buffer Area | 25 | 35 | 65 | 25 | 35 | 1-P056
27 | Module 2 | 1-P058 | Washing Room | 25 |  |  | 10 | 20 | 1-P053
28 | Module 2 | 1-P057 | Cleaned Equipment Storage | 25 | 35 | 65 | 40 | 50 | 1-P056
29 | Module 2 | 1-P059 | Spare Room | 25 | 35 | 45 | 10 | 20 | 1-P053
30 | Module 2 | 1-P060 | Binder Preparation Room | 25 | 30 | 50 | 10 | 20 | 1-P053
31 | Module 2 | 1-P061 | Granulation Room | 25 | 30 | 50 | 10 | 20 | 1-P053
32 | Module 2 | 1-P062 | Mixing Room | 25 | 25 | 30 | 10 | 20 | 1-P053
33 | Module 2 | 1-P063 | Granule Storage | 25 | 35 | 65 | 10 | 20 | 1-P053
34 | Module 2 | 1-P064 | Capsule Filling Room 1 | 25 | 25 | 30 | 10 | 20 | 1-P053
35 | Module 2 | 1-P065 | Capsule Filling Room 2 | 25 | 35 | 45 | 10 | 20 | 1-P053
36 | Module 2 | 1-P066 | In Process Control Room | 25 | 35 | 65 | 10 | 20 | 1-P053
37 | Module 2 | 1-P067 | Capsule Storage Room | 25 | 35 | 65 | 10 | 20 | 1-P053
38 | Module 2 | 1-P068 | Weight Checking Room 2 | 25 | 35 | 65 | 10 | 20 | 1-P053
39 | Module 2 | 1-P070 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 1-P053
40 | Module 2 | 1-P071 | Janitor Room | 25 |  |  | 10 | 20 | 1-P053
41 | Module 2 | 1-P074 | Janitor Room | 25 |  |  |  |  | 1-P053
42 | Module 2 | 1-P069 | Machine Exit | 25 | 35 | 65 | 10 | 20 | 1-P053
43 | Module 2 | 1-P073 | Airlock 2 | 25 | 35 | 65 | 40 | 50 | 1-P053
44 | Packing Floor 1 | 1-P050 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 1-P082
45 | Packing Floor 1 | 1-P075 | Janitor Room | 25 |  |  | 10 | 20 | 1-P082
46 | Packing Floor 1 | 1-P079 | In Process Control Room | 25 | 35 | 65 | 10 | 20 | 1-P082
47 | Packing Floor 1 | 1-P076 | Changing Room 1 | 25 |  |  | 10 | 20 | 1-P082
48 | Packing Floor 1 | 1-P077 | Changing Room 2 | 25 |  |  | 10 | 20 | 1-P082
49 | Packing Floor 1 | 1-P078 | Laundry | 25 |  |  | 25 | 35 | 1-P082
50 | Packing Floor 1 | 1-P080 | Packing Room 4 | 25 | 30 | 50 | 10 | 20 | 1-P082
51 | Packing Floor 1 | 1-P082 | Corridor | 25 | 35 | 65 | 25 | 35 | 1-P082
52 | Packing Floor 1 | 1-P083 | Packing Room 1 | 25 | 35 | 65 | 10 | 20 | 1-P082
53 | Packing Floor 1 | 1-P084 | Packing Room 2 | 25 | 35 | 65 | 10 | 20 | 1-P082
54 | Packing Floor 1 | 1-P085 | Inspection Room | 25 | 30 | 50 | 10 | 20 | 1-P082
55 | Packing Floor 1 | 1-P087 | Bulk Storage 1 | 25 | 35 | 65 | 10 | 20 | 1-P082
56 | Packing Floor 1 | 1-P086 | Packing Room 3 | 25 | 35 | 65 | 10 | 20 | 1-P082
57 | Packing Floor 1 | 1-P088 | Bulk Storage 2 | 25 | 35 | 65 | 10 | 20 | 1-P082
58 | Packing Floor 1 | 1-P089 | Secondary Packing Area | 25 |  |  |  |  | 1-P089
59 | Packing Floor 1 | 1-P149 | Bulk Storage 3 | 25 | 30 | 50 | 10 | 20 | 1-P166
60 | Packing Floor 1 | 1-P166 | Corridor | 25 | 35 | 65 | 25 | 35 | 1-P166
61 | Dispensing Area | 1-W093 | Changing Room 1 | 25 | 35 | 65 | 10 | 20 | 1-W108
62 | Dispensing Area | 1-W094 | Material Entrance 1 | 25 | 35 | 65 | 10 | 20 | 1-W108
63 | Dispensing Area | 1-W092 | Dispensing Room 1 | 25 | 30 | 50 | 10 | 20 | 1-W108
64 | Dispensing Area | 1-W096 | Changing Room 2 | 25 | 35 | 65 | 10 | 20 | 1-W108
65 | Dispensing Area | 1-W097 | Material Entrance 2 | 25 | 35 | 65 | 10 | 20 | 1-W108
66 | Dispensing Area | 1-W095 | Dispensing Room 2 | 25 | 25 | 30 | 10 | 20 | 1-W108
67 | Dispensing Area | 1-W099 | Changing Room 3 | 25 | 35 | 65 | 10 | 20 | 1-W108
68 | Dispensing Area | 1-W100 | Material Entrance 3 | 25 | 35 | 65 | 10 | 20 | 1-W108
69 | Dispensing Area | 1-W098 | Dispensing Room 3 | 25 | 35 | 65 | 10 | 20 | 1-W108
70 | Dispensing Area | 1-W102 | Changing Room 4 | 25 | 35 | 65 | 10 | 20 | 1-W108
71 | Dispensing Area | 1-W103 | Material Entrance 4 | 25 | 35 | 65 | 10 | 20 | 1-W108
72 | Dispensing Area | 1-W101 | Dispensing Room 4 | 25 | 35 | 65 | 10 | 20 | 1-W108
73 | Dispensing Area | 1-W105 | Changing Room 5 | 25 | 35 | 65 | 10 | 20 | 1-W108
74 | Dispensing Area | 1-W106 | Material Entrance 5 | 25 | 35 | 65 | 10 | 20 | 1-W108
75 | Dispensing Area | 1-W104 | Dispensing Room 5 | 25 | 35 | 45 | 10 | 20 | 1-W108
76 | Dispensing Area | 1-W107 | Staging Area | 25 | 35 | 65 |  |  | 1-W108
77 | Dispensing Area | 1-W108 | Dispensing Corridor | 25 | 35 | 65 | 25 | 35 | 1-W108
78 | Dispensing Area | 1-W128 | Solvent Dispensing Room | 25 | 35 | 65 | 40 | 50 | 1-W108
79 | Dispensing Area | 1-W109 | Changing Room 6 | 25 | 35 | 65 | 40 | 50 | 1-W108
80 | Dispensing Area | 1-W110 | Material Entrance 6 | 25 | 35 | 65 | 40 | 50 | 1-W108
81 | Dispensing Area | 1-W111 | Janitor Room | 25 | 35 | 65 | 10 | 20 | 1-W108
82 | Dispensing Area | 1-W112 | Material Entrance 7 | 25 | 35 | 65 | 10 | 20 | 1-W108
83 | Dispensing Area | 1-W114 | Changing Room 7 | 25 | 35 | 65 | 10 | 20 | 1-W108
84 | Dispensing Area | 1-W113 | Material Entrance 8 | 25 | 35 | 65 | 10 | 20 | 1-W108
85 | Dispensing Area | 1-W117 | RM Sampling Room 2 | 25 | 35 | 65 | 10 | 20 | 1-W108
86 | Dispensing Area | 1-W119 | Changing Room 9 | 25 | 35 | 65 | 10 | 20 | 1-W108
87 | Dispensing Area | 1-W115 | RM Sampling Corridor | 25 | 35 | 65 | 25 | 35 | 1-W108
88 | Dispensing Area | 1-W116 | RM Sampling Room 1 | 25 | 25 | 30 | 10 | 20 | 1-W108
89 | Dispensing Area | 1-W118 | Changing Room 8 | 25 | 35 | 65 | 10 | 20 | 1-W108
90 | Dispensing Area | 1-W120 | Washing Room | 25 |  |  | 10 | 20 | 1-W108
91 | Dispensing Area | 1-W121 | Cleaned Equipment Storage | 25 | 35 | 65 | 40 | 50 | 1-W108
92 | Dispensing Area | 1-W122 | Airlock | 25 | 35 | 65 | 10 | 20 | 1-W108
93 | Warehouse Area | 1-W127 | Stationery Room | 25 |  |  |  |  | 1-W127
94 | Warehouse Area | 1-W138 | FG Storage | 25 | 35 | 65 |  |  | 1-W138
95 | Warehouse Area | 1-W139 | PM Storage | 25 | 35 | 65 |  |  | 1-W139
96 | Warehouse Area | 1-W140 | RM Storage | 25 | 35 | 65 |  |  | 1-W140
97 | Warehouse Area | 1-W123 | PM Sampling Room 1 | 25 | 35 | 65 | -5 | 5 | 1-W123
98 | Warehouse Area | 1-W124 | PM Sampling Corridor | 25 | 35 | 65 | -5 | 5 | 1-W124
99 | Warehouse Area | 1-W125 | Changing Room 10 | 25 | 35 | 65 | -5 | 5 | 1-W125
100 | Warehouse Area | 1-W126 | PM Sampling Room 2 | 25 | 35 | 65 | -5 | 5 | 1-W126
101 | IPA Plant | 1-W151 | Changing room 11 | 25 |  |  | 10 | 20 | 1-W153
102 | IPA Plant | 1-W152 | Changing room 12 | 25 |  |  | 10 | 20 | 1-W153
103 | IPA Plant | 1-W153 | Main corridor | 25 |  |  | 25 | 35 | 1-W153
104 | IPA Plant | 1-W154 | Dispensing airlock | 25 |  |  | 40 | 50 | 1-W153
105 | IPA Plant | 1-W155 | Solvent dispensing room | 25 |  |  | 25 | 35 | 1-W153
106 | IPA Plant | 1-W156 | Washing room | 25 |  |  | 10 | 20 | 1-W153
107 | IPA Plant | 1-W157 | Janitor room | 25 |  |  | 10 | 20 | 1-W153
108 | IPA Plant | 1-W158 | Cleaned equipment room | 25 |  |  | 40 | 50 | 1-W153
109 | IPA Plant | 1-W159 | Sampling corridor | 25 |  |  | 25 | 35 | 1-W153
110 | IPA Plant | 1-W160 | Buffer area | 25 |  |  | 40 | 50 | 1-W153
111 | IPA Plant | 1-W161 | Solvent sampling room | 25 |  |  | 25 | 35 | 1-W153
112 | IPA Plant | 1-W162 | Sampling material entrance | 25 |  |  | 10 | 20 | 1-W153
113 | IPA Plant | 1-W163 | Dispensing material entrance | 25 |  |  | 10 | 20 | 1-W153
114 | IPA Plant | 1-W164 | Storage corridor | 25 |  |  | -5 | 5 | 1-W153
115 | Lab Area | 2-L021 | Identification Room | 25 | 35 | 65 | -5 | 5 | 2-L021
116 | Lab Area | 2-L019 | Changing Room 2 | 25 | 35 | 65 | -5 | 5 | 2-L019
117 | Lab Area | 2-L020 | Airlock 2 | 25 | 35 | 65 | 10 | 20 | 2-L020
118 | Lab Area | 2-L016 | MET Room | 25 | 35 | 65 | 25 | 35 | 2-L016
119 | Lab Area | 2-L014 | Changing Room 1 | 25 | 35 | 65 | 10 | 20 | 2-L014
120 | Lab Area | 2-L015 | Airlock 1 | 25 | 35 | 65 | 25 | 35 | 2-L015
121 | Module 3 | 2-P071 | Corridor | 25 | 35 | 65 | 25 | 35 | 2-P071
122 | Module 3 | 2-P072 | Airlock 1 | 25 | 35 | 65 | 10 | 20 | 2-P074
123 | Module 3 | 2-P073 | Changing Room | 25 | 35 | 65 | 10 | 20 | 2-P074
124 | Module 3 | 2-P074 | Buffer Area | 25 | 35 | 65 | 25 | 35 | 2-P074
125 | Module 3 | 2-P075 | Cleaned Equipment Storage | 25 | 35 | 65 | 40 | 50 | 2-P074
126 | Module 3 | 2-P076 | Washing Room | 25 |  |  | 10 | 20 | 2-P071
127 | Module 3 | 2-P077 | Mixing Room | 25 | 35 | 65 | 10 | 20 | 2-P071
128 | Module 3 | 2-P078 | Tableting Room 1 | 25 | 35 | 65 | 10 | 20 | 2-P071
129 | Module 3 | 2-P079 | Tableting Room 2 | 25 | 35 | 65 | 10 | 20 | 2-P071
130 | Module 3 | 2-P080 | Granule Storage | 25 | 35 | 65 | 10 | 20 | 2-P071
131 | Module 3 | 2-P081 | Inspection Room | 25 | 35 | 65 | 10 | 20 | 2-P071
132 | Module 3 | 2-P082 | In Process Control Room | 25 | 35 | 65 | 10 | 20 | 2-P071
133 | Module 3 | 2-P083 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 2-P071
134 | Module 3 | 2-P084 | Janitor Room | 25 |  |  | 10 | 20 | 2-P071
135 | Module 3 | 2-P085 | Machine Exit | 25 |  |  | 10 | 20 | 2-P071
136 | Module 3 | 2-A086 | Janitor Room 2 | 25 |  |  |  |  | 2-P071
137 | Module 3 | 2-P093 | Airlock 2 | 25 | 35 | 65 | 40 | 50 | 2-P071
138 | Module 4 | 2-P051 | Airlock | 25 | 35 | 65 | 10 | 20 | 2-P053
139 | Module 4 | 2-P052 | Changing Room | 25 | 35 | 65 | 10 | 20 | 2-P053
140 | Module 4 | 2-P053 | Buffer Area | 25 | 35 | 65 | 25 | 35 | 2-P053
141 | Module 4 | 2-P055 | Cleaned Equipment Storage | 25 | 35 | 65 | 40 | 50 | 2-P053
142 | Module 4 | 2-P056 | Washing Room | 25 |  |  | 10 | 20 | 2-P069
143 | Module 4 | 2-P054 | Janitor Room | 25 | 35 | 65 | 10 | 20 | 2-P053
144 | Module 4 | 2-P057 | Binder Preparation Room | 25 | 35 | 65 | 10 | 20 | 2-P069
145 | Module 4 | 2-P058 | Granulation Room | 25 | 35 | 55 | 10 | 20 | 2-P069
146 | Module 4 | 2-P059 | Mixing Room | 25 | 35 | 55 | 10 | 20 | 2-P069
147 | Module 4 | 2-P060 | Granule Storage | 25 | 35 | 60 | 10 | 20 | 2-P069
148 | Module 4 | 2-P061 | Tableting Room 1 | 25 | 35 | 55 | 10 | 20 | 2-P069
149 | Module 4 | 2-P062 | Tableting Room 2 | 25 | 35 | 60 | 10 | 20 | 2-P069
150 | Module 4 | 2-P063 | In Process Control Room | 25 | 35 | 65 | 10 | 20 | 2-P069
151 | Module 4 | 2-P064 | Core Tablet Storage | 25 | 35 | 55 | 10 | 20 | 2-P069
152 | Module 4 | 2-P065 | Coating Preparation Room | 25 |  |  | 10 | 20 | 2-P069
153 | Module 4 | 2-P066 | Coating Room 1 | 25 | 35 | 65 | 10 | 20 | 2-P069
154 | Module 4 | 2-P067 | Coating Room 2 | 25 | 35 | 65 | 10 | 20 | 2-P069
155 | Module 4 | 2-P068 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 2-P069
156 | Module 4 | 2-P069 | Corridor | 25 | 35 | 65 | 25 | 35 | 2-P069
157 | Module 4 | 2-P070 | Corridor | 25 | 35 | 65 | 25 | 35 | 2-P070
158 | Packing Floor 2 | 2-P087 | Bulk Storage | 25 | 35 | 65 | 10 | 20 | 2-P092[082}
159 | Packing Floor 2 | 2-P088 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 2-P092[082}
160 | Packing Floor 2 | 2-P089 | In Process Control Room | 25 |  |  | 10 | 20 | 2-P092[082}
161 | Packing Floor 2 | 2-P091 | Janitor Room | 25 |  |  | 10 | 20 | 2-P092[082}
162 | Packing Floor 2 | 2-P090 | Changing Room | 25 | 35 | 65 | 10 | 20 | 2-P092[082}
163 | Packing Floor 2 | 2-P092[082} | Corridor | 25 | 35 | 65 | 25 | 35 | 2-P092[082}
164 | Packing Floor 2 | 2-P092[083} | Corridor | 25 | 35 | 65 | 25 | 35 | 2-P092[083}
165 | Packing Floor 2 | 2-P094 | Packing Room 1 | 25 | 35 | 65 | 10 | 20 | 2-P092[083}
166 | Packing Floor 2 | 2-P095 | Packing Room 2 | 25 | 35 | 65 | 10 | 20 | 2-P092[083}
167 | Packing Floor 2 | 2-P096 | Inspection Room | 25 | 35 | 65 | 10 | 20 | 2-P092[083}
168 | Packing Floor 2 | 2-P097 | Packing Room 3 | 25 | 35 | 65 | 10 | 20 | 2-P092[083}
169 | Packing Floor 2 | 2-P098 | Packing Room 4 | 25 | 35 | 65 | 10 | 20 | 2-P092[083}
170 | Packing Floor 2 | 2-P099 | Secondary Packing Area | 25 |  |  |  |  | 2-P092[082}
171 | Module 5 | M5 2-P166 | Corridor 7 | 25 | 35 | 65 | 25 | 35 | M5 2-P166
172 | Module 5 | M5 2-P167 | Janitor Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P166
173 | Module 5 | M5 2-P168 | Changing Room 9 | 25 | 35 | 65 | 25 | 35 | M5 2-P166
174 | Module 5 | M5 2-P169 | Airlock 9 | 25 | 35 | 65 | 25 | 35 | M5 2-P166
175 | Module 5 | M5 2-P170 | Primary Packing Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P166
176 | Module 5 | M5 2-P171 | Airlock 10 | 25 | 35 | 65 | 25 | 35 | M5 2-P166
177 | Module 5 | M5 2-P172 | Changing Room 10 | 25 | 35 | 65 | 25 | 35 | M5 2-P166
178 | Module 5 | M5 2-P173 | Primary Packing Room 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P166
179 | Module 5 | M5 2-P141 | Changing Room 5 | 25 | 35 | 65 | 25 | 35 | M5 2-P143
180 | Module 5 | M5 2-P142 | Coating Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P143
181 | Module 5 | M5 2-P143 | Corridor 4 | 25 | 35 | 65 | 25 | 35 | M5 2-P143
182 | Module 5 | M5 2-P144 | Coating Preparation Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P143
183 | Module 5 | M5 2-P145 | Coating Preparation Room 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P143
184 | Module 5 | M5 2-P146 | Coating Room 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P143
185 | Module 5 | M5 2-P147 | Airlock 5 | 25 | 35 | 65 | 25 | 35 | M5 2-P143
186 | Module 5 | M5 2-P136 | Airlock 4 | 25 | 35 | 65 | 25 | 35 | M5 2-P138
187 | Module 5 | M5 2-P137 | Changing Room 4 | 25 | 35 | 65 | 25 | 35 | M5 2-P138
188 | Module 5 | M5 2-P138 | Corridor 3 | 25 | 35 | 65 | 25 | 35 | M5 2-P138
189 | Module 5 | M5 2-P139 | Tableting Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P138
190 | Module 5 | M5 2-P140 | Inprocess Control Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P138
191 | Module 5 | M5 2-P128 | Changing Room 2 | 25 | 35 | 65 | 25 | 35 | M5 2-P131
192 | Module 5 | M5 2-P129 | Airlock 2 | 25 | 35 | 65 | 25 | 35 | M5 2-P131
193 | Module 5 | M5 2-P130 | Binder Preparation Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P131
194 | Module 5 | M5 2-P131 | Corridor 2 | 25 | 35 | 65 | 25 | 35 | M5 2-P131
195 | Module 5 | M5 2-P132 | Granulation Room 1 (Closed transfer system) | 25 | 35 | 65 | 10 | 20 | M5 2-P131
196 | Module 5 | M5 2-P161 | Granule Storage Room | 25 | 35 | 65 | 10 | 20 | M5 2-P127
197 | Module 5 | M5 2-P162 | Washing Room | 25 | 35 | 65 | 10 | 20 | M5 2-P127
198 | Module 5 | M5 2-P163 | Cleaned Equipment Storage Room | 25 | 35 | 65 | 40 | 50 | M5 2-P127
199 | Module 5 | M5 2-P164 | Bulk Storage Room | 25 | 35 | 65 | 10 | 20 | M5 2-P127
200 | Module 5 | M5 2-P165 | Change Part Storage Room | 25 | 35 | 65 | 40 | 50 | M5 2-P127
201 | Module 5 | M5 2-P183 | Secondary Packing Room 1 | 25 |  |  |  |  | M5 2-P183
202 | Module 5 | M5 2-P184 | Secondary Packing Room 2 | 25 |  |  |  |  | M5 2-P184
203 | Module 5 | M5 2-P185 | Secondary Packing Room 3 | 25 |  |  |  |  | M5 2-P185
204 | Module 5 | M5 2-P186 | Secondary Packing Room 4 | 25 |  |  |  |  | M5 2-P186
205 | Module 5 | M5 2-P187 | Outer Corridor | 25 |  |  |  |  | M5 2-P187
206 | Module 5 | M5 2-P133 | Airlock 3 | 25 | 35 | 65 | 25 | 35 | M5 2-P127
207 | Module 5 | M5 2-P134 | Changing Room 3 | 25 | 35 | 65 | 25 | 35 | M5 2-P127
208 | Module 5 | M5 2-P135 | Dry Mixing Room | 25 | 35 | 65 | 10 | 20 | M5 2-P127
209 | Module 5 | M5 2-P148 | Changing Room 6 | 25 | 35 | 65 | 25 | 35 | M5 2-P127
210 | Module 5 | M5 2-P149 | Airlock 6 | 25 | 35 | 65 | 25 | 35 | M5 2-P151
211 | Module 5 | M5 2-P150 | Binder Preparation Room 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P151
212 | Module 5 | M5 2-P151 | Corridor 5 | 25 | 35 | 65 | 25 | 35 | M5 2-P151
213 | Module 5 | M5 2-P152 | Granulation Room 2 (Closed transfer system) | 25 | 35 | 65 | 10 | 20 | M5 2-P151
214 | Module 5 | M5 2-P123 | Changing Room 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P127
215 | Module 5 | M5 2-P124 | Airlock 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P127
216 | Module 5 | M5 2-P125 | PD Office 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P127
217 | Module 5 | M5 2-P126 | PD Office 1 | 25 | 35 | 65 | 10 | 20 | M5 2-P127
218 | Module 5 | M5 2-P127 | Corridor 1 | 25 | 35 | 65 | 25 | 35 | M5 2-P127
219 | Module 5 | M5 2-P153 | Changing Room 7 | 25 | 35 | 65 | 25 | 35 | M5 2-P155
220 | Module 5 | M5 2-P154 | Airlock 7 | 25 | 35 | 65 | 25 | 35 | M5 2-P155
221 | Module 5 | M5 2-P155 | Corridor 6 | 25 | 35 | 65 | 25 | 35 | M5 2-P155
222 | Module 5 | M5 2-P156 | Tableting Room 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P155
223 | Module 5 | M5 2-P157 | Inprocess Control Room 2 | 25 | 35 | 65 | 10 | 20 | M5 2-P155
224 | Module 5 | M5 2-P158 | Airlock 8 | 25 | 35 | 65 | 25 | 35 | M5 2-P127
225 | Module 5 | M5 2-P159 | Changing Room 8 | 25 | 35 | 65 | 25 | 35 | M5 2-P127
226 | Module 5 | M5 2-P160 | Inspection Room | 25 | 35 | 65 | 10 | 20 | M5 2-P127
227 | Module 5 | M5 2-P174 | Corridor 8 | 25 | 35 | 65 | 25 | 35 | M5 2-P174
228 | Module 5 | M5 2-P175 | Inprocess Control Room 3 | 25 | 35 | 65 | 10 | 20 | M5 2-P174
229 | Module 5 | M5 2-P176 | Airlock 11 | 25 | 35 | 65 | 25 | 35 | M5 2-P174
230 | Module 5 | M5 2-P177 | Changing Room 11 | 25 | 35 | 65 | 25 | 35 | M5 2-P174
231 | Module 5 | M5 2-P178 | Primary Packing Room 3 | 25 | 35 | 65 | 10 | 20 | M5 2-P174
232 | Module 5 | M5 2-P179 | Airlock 12 | 25 | 35 | 65 | 25 | 35 | M5 2-P174
233 | Module 5 | M5 2-P180 | Changing Room 12 | 25 | 35 | 65 | 25 | 35 | M5 2-P174
234 | Module 5 | M5 2-P181 | Primary Packing Room 4 | 25 | 35 | 65 | 10 | 20 | M5 2-P174
235 | Module 5 | M5 2-P182 | Airlock 13 | 25 | 35 | 65 | 10 | 20 | M5 2-P174
236 | Pilot scale | 1-S032 | Secondary Packing Room | 25 |  |  |  |  | 1-S032
237 | Pilot scale | 1-S029 | Primary Packing Room 1 | 25 | 30 | 50 | 10 | 20 | 1-S008
238 | Pilot scale | 1-S030 | Material Entrance 7 | 25 | 35 | 65 | 25 | 35 | 1-S008
239 | Pilot scale | 1-S031 | Changing Room 7 | 25 | 35 | 65 | 25 | 35 | 1-S008
240 | Pilot scale | 1-S025 | Bulk Storage | 25 | 30 | 65 | 10 | 20 | 1-S008
241 | Pilot scale | 1-S021 | In Process Control Room | 25 | 35 | 65 | 10 | 20 | 1-S008
242 | Pilot scale | 1-S016 | Airlock 3 | 25 | 35 | 65 | 10 | 20 | 1-S008
243 | Pilot scale | 1-S014 | Airlock 1 | 25 | 35 | 65 | 10 | 20 | 1-S008
244 | Pilot scale | 1-S008 | Corridor Floor 1 | 25 | 30 | 65 | 25 | 35 | 1-S008
245 | Pilot scale | 1-S009 | Change Part Storage | 25 | 35 | 65 | 40 | 50 | 1-S008
246 | Pilot scale | 1-S010 | Changing Room 3 | 25 | 35 | 65 | 25 | 35 | 1-S008
247 | Pilot scale | 1-S011 | Material Entrance 3 | 25 | 35 | 65 | 25 | 35 | 1-S008
248 | Pilot scale | 1-S012 | Washing Room 1 | 25 | 35 | 65 | 10 | 20 | 1-S008
249 | Pilot scale | 1-S033 | Drying Room 1 | 25 | 30 | 65 | 25 | 35 | 1-S008
250 | Pilot scale | 1-S013 | Clean Equipment Storage 1 | 25 | 35 | 65 | 40 | 50 | 1-S008
251 | Pilot scale | 1-S015 | Airlock 2 | 25 | 35 | 65 | 25 | 35 | 1-S008
252 | Pilot scale | 1-S002 | Changing Room 1 | 25 | 35 | 65 | 25 | 35 | 1-S008
253 | Pilot scale | 1-S003 | Material Entrance 1 | 25 | 35 | 65 | 25 | 35 | 1-S008
254 | Pilot scale | 1-S004 | Changing Room 2 | 25 | 35 | 65 | 25 | 35 | 1-S008
255 | Pilot scale | 1-S005 | Material Entrance 2 | 25 | 35 | 65 | 25 | 35 | 1-S008
256 | Pilot scale | 1-S006 | Weight Checking Room | 25 | 30 | 65 | 10 | 20 | 1-S008
257 | Pilot scale | 1-S007 | Staging Room | 25 | 30 | 65 | 10 | 20 | 1-S008
258 | Pilot scale | 1-S018 | Changing Room 4 | 25 | 35 | 65 | 25 | 35 | 1-S008
259 | Pilot scale | 1-S019 | Material Entrance 4 | 25 | 35 | 65 | 25 | 35 | 1-S008
260 | Pilot scale | 1-S023 | Changing Room 5 | 25 | 35 | 65 | 25 | 35 | 1-S008
261 | Pilot scale | 1-S022 | Material Entrance 5 | 25 | 35 | 65 | 25 | 35 | 1-S008
262 | Pilot scale | 1-S027 | Changing Room 6 | 25 | 35 | 65 | 25 | 35 | 1-S008
263 | Pilot scale | 1-S026 | Material Entrance 6 | 25 | 35 | 65 | 25 | 35 | 1-S008
264 | Pilot scale | 1-S028 | Primary Packing Room 2 | 25 | 30 | 65 | 10 | 20 | 1-S008
265 | Pilot scale | 1-S024 | Tableting Room 1 | 25 | 30 | 50 | 10 | 20 | 1-S008
266 | Pilot scale | 1-S001 | Tableting Room 2 | 25 | 30 | 65 | 10 | 20 | 1-S008
267 | Pilot scale | 2-S022 | Mixing room | 25 | 30 | 50 | 10 | 20 | 2-S004
268 | Pilot scale | 1-S020 | Coating Room | 25 | 30 | 50 | 10 | 20 | 1-S008
269 | Pilot scale | 1-S017 | Coating Preparation Room | 25 | 30 | 50 | 10 | 20 | 1-S008
270 | Pilot scale | 2-S031 | Granulation Room | 25 | 30 | 65 | 10 | 20 | 2-S004
271 | Pilot scale | 2-S030 | Binder Preparation Room | 25 | 30 | 65 | 10 | 20 | 2-S004
272 | Pilot scale | 2-S009 | Airlock 4 | 25 | 35 | 65 | 25 | 35 | 2-S004
273 | Pilot scale | 2-S032 | Corridor (บันได) | 25 | 35 | 65 | 10 | 20 | 2-S004
274 | Pilot scale | 2-S013 | Changing Room 9 | 25 | 35 | 65 | 25 | 35 | 2-S004
275 | Pilot scale | 2-S012 | Material Entrance 9 | 25 | 35 | 65 | 25 | 35 | 2-S004
276 | Pilot scale | 2-S014 | Dry Granulation Room | 25 | 30 | 50 | 10 | 20 | 2-S004
277 | Pilot scale | 2-S017 | Changing Room 10 | 25 | 35 | 65 | 25 | 35 | 2-S004
278 | Pilot scale | 2-S016 | Material Entrance 10 | 25 | 35 | 65 | 25 | 35 | 2-S004
279 | Pilot scale | 2-S018 | Washing Room 2 | 25 | 35 | 65 | 10 | 20 | 2-S004
280 | Pilot scale | 2-S021 | Drying Room 2 | 25 | 30 | 65 | 25 | 35 | 2-S004
281 | Pilot scale | 2-S025 | Clean Equipment Storage 2 | 25 | 35 | 65 | 40 | 50 | 2-S004
282 | Pilot scale | 2-S020 | Janitor Room | 25 | 35 | 65 | 10 | 20 | 2-S004
283 | Pilot scale | 2-S029 | Changing Room 12 | 25 | 35 | 65 | 25 | 35 | 2-S004
284 | Pilot scale | 2-S028 | Material Entrance 12 | 25 | 35 | 65 | 25 | 35 | 2-S004
285 | Pilot scale | 2-S027 | Office | 25 | 35 | 65 | 10 | 20 | 2-S004
286 | Pilot scale | 2-S026 | PD Office | 25 | 35 | 65 | 10 | 20 | 2-S004
287 | Pilot scale | 2-S002 | Changing Room | 25 | 35 | 65 | 10 | 20 | 2-S004
288 | Pilot scale | 2-S006 | Changing Room 8 | 25 | 35 | 65 | 25 | 35 | 2-S004
289 | Pilot scale | 2-S007 | Material Entrance 8 | 25 | 35 | 65 | 25 | 35 | 2-S004
290 | Pilot scale | 2-S005 | Capsule Filling Room | 25 | 30 | 65 | 10 | 20 | 2-S004
291 | Pilot scale | 2-S011 | Airlock 5 | 25 | 35 | 65 | 10 | 20 | 2-S004
292 | Pilot scale | 2-S015 | Airlock 6 | 25 | 35 | 65 | 25 | 35 | 2-S004
293 | Pilot scale | 2-S010 | Sample Storage Room | 25 | 30 | 65 | 10 | 20 | 2-S004
294 | Pilot scale | 2-S019 | Granule Storage | 25 | 30 | 65 | 10 | 20 | 2-S004
295 | Pilot scale | 2-S024 | Changing Room 11 | 25 | 35 | 65 | 25 | 35 | 2-S004
296 | Pilot scale | 2-S023 | Material Entrance 11 | 25 | 35 | 65 | 25 | 35 | 2-S004
297 | Pilot scale | 2-S004 | Corridor Floor 2 | 25 | 30 | 65 | 25 | 35 | 2-S004