Master Validation Plan (MVP): Air Quality Review System

| Document Control Information | Details |
| --- | --- |
| Project/System Name | Air Quality Review System (AQR) |
| System Identifier | AQR-SYS-01 |
| GAMP 5 Category | Category 5 (Custom Built Application) |
| Regulatory Context | GMP, 21 CFR Part 11, EU GMP Annex 11, PIC/S PI 011-3 |
| Document Version | 1.0 |
| Date of Creation | 2026-04-22 |

- Introduction

The Air Quality Review (AQR) System is a custom-developed Python application designed to automate the compliance review of environmental monitoring data (Temperature, Humidity, Differential Pressure). The system evaluates raw CSV data from the Building Automation System (BAS) of Rangsit Pharmaceutical Production Plant I against predefined limits (SetPointLimit.xlsx) which defined the condition specification of each location to identify GxP excursions, enforcing a complex "25-Minute Continuous Violation Rule" and "Pressure Corridor Comparison".

This Master Validation Plan (MVP) defines the strategy to validate the system, ensuring it is "fit for intended use" and complies with 21 CFR Part 11.

- System Description and Boundaries

  - System Architecture & Delivery

The system is developed using Python, Pandas, and Flask. For production deployment, it is compiled and delivered as a Standalone Executable using PyInstaller. This ensures a controlled, immutable runtime environment that does not require a Python interpreter on the end-user's machine.

  - System Boundaries

- Inbound Boundary: Raw CSV data files exported from the BAS placed into the target directory.

- System Boundary: The execution of app.exe, encompassing all embedded business logic, UI rendering, and data transformation.

- Outbound Boundary: The generation of the Excel summary report and the cryptographic sealing of the audit_trail.log.

- Scope of Validation

- Application Logic: All data processing, deduplication, point mapping, the 25-minute rule algorithms.

- Data Integrity & Security: Tamper-evident Hash-chained Audit Trails, source CSV SHA-256 hashing, and Limit File (SetPointLimit.xlsx) version tracking.

- Deployment Integrity: The reproducibility of the app.exe build and its correct path resolution during runtime.

- Regulatory Strategy (21 CFR Part 11)

The AQR System is classified as a Hybrid System:

- 11.10(c) Record Protection: Source CSV files are strictly accessed in "Read-Only" mode. Audit logs utilize blockchain-like hash chaining.

- 11.10(d) System Access: Access to execute the .exe is restricted via Windows Active Directory (AD) folder permissions.

- 11.10(e) Audit Trail: A secure, timestamped audit log captures User, Action, File Hashes, and Limit File modifications. A mandatory SOP requires periodic review of this log.

- Validation Methodology (GAMP 5)

- The validation strictly adheres to the ISPE GAMP 5 Second Edition V-Model:

- 4-Agent Validation Committee: All deliverables are reviewed iteratively by a GMP Specialist, CSV Specialist, Documentation Specialist, and Coding Specialist (Powered by Gemini 3.1 Ultra eiei krirki ).

- Risk Assessment: Functional Risk Assessment (FRA) via FMEA methodology.

- Deliverables and Acceptance Criteria

- Validation Phases

- Phase 1 (Planning): VP, URS

- Phase 2 (Risk & Function): FRA, FS

- Phase 3 (Design): DS, CS

- Phase 4 (Installation): IQ, CRR

- Phase 5 (Operation): OQ

- Phase 6 (Performance): PQ, RTM, VSR

- Acceptance Criteria

- 100% Traceability: All User Requirements must be traced to approved OQ/PQ test cases.

- Deviation Management: Zero open critical or major deviations at the time of system release.