Enclosure 2: Test Script

| Test ID | Test Scenario | Expected Result |
| --- | --- | --- |
| OQ-TC-01 | To verify that the system correctly subtracts one day from the date found in the raw data filename. Many sensors save data for "Yesterday" at 00:05 AM "Today." To make sure the report shows the correct day the air was actually measured, the system must automatically move the date back by one day. | - The cell "Date of Review" correctly displays the value " 05 Apr 2026". |
| OQ-TC-04 | To verify that 6 consecutive points (25 mins) above the limit trigger a failure. | - Result status in the report shows: `Out of Spec` (✗) and `Passed` (✓) respectively. |
| OQ-TC-05 | To verify that missing data points prevent a violation from being reported. | - Result status in the report shows: `Passed` (✓) caused by the system correctly identifies that there was no continuous 25-minute violation. |
| OQ-TC-06 | Confirm that sustained high humidity (above 65%) is flagged correctly. | - Result status in the report shows: `Out of Spec` (✗) and `Passed` (✓) respectively. |
| OQ-TC-07 | Confirm that sustained low humidity (below 35%) is flagged correctly. | - Result status in the report shows: `Out of Spec` (✗) and `Passed` (✓) respectively. |
| OQ-TC-08 | To verify that missing data points prevent a violation from being reported. | - Result status in the report shows: `Passed` (✓) caused by the system correctly identifies that there was no continuous 25-minute violation. |
| OQ-TC-09 | To verify that the system can detect the separate low/high out of the limit and reporting in the separating format. | - Result status in the report shows: `Out of Spec` (✗) followed by detailed separating interval that relative humidity out of low limit and high limit. |
| OQ-TC-10 | Verify that the system flags a room when its pressure is lower than the corridor pressure. | - Result status in the report shows: `Passed` (✓) and status string shows: `within` Corridor. |
| OQ-TC-11 | Verify that if a room is over its own internal limit and above the corridor, it is flagged as 'over'. | - Result status in the report shows: `Out of Spec` (✗) and status string shows: `over` Corridor. |
| OQ-TC-12 | Verify that the system flags a room when its pressure is higher than the corridor pressure. | - Result status in the report shows: `Passed` (✓) and status string shows: `over` Corridor. |
| OQ-TC-13 | Verify that if a room is over its own internal limit and below the corridor, it is flagged as 'under'. | - Result status in the report shows: `Out of Spec` (✗) and status string shows: `under` Corridor. |
| OQ-TC-14 | To verify that the system can split a bulk Main Plant (RMT, RMH, and RPT), Module 5, Pilot scale files into individual room CSVs. | - A new folder has been created with a timestamped name. - The folder contains individual CSV files, one for each room for number equal to bulk CSV file. |
| OQ-TC-15 | To ensure the report only contains data points within the selected date range. | - The final Excel report only displays rows with timestamps from March 1st to March 5th. |
| OQ-TC-16 | Verify the system can ignore specific rooms if they are not selected in the checklist. | - The final Excel report does not contain any data or sheets for Module 1. |
| OQ-TC-17 | Verify that the system skips "garbage" data (like "Data Loss" or "No Data") without crashing. | - The system completes the analysis without errors. - Result status in the report shows: `Data Loss` and period of its. - A "Warning" entry regarding the non-numeric data is recorded in `audit_trail.log`. |
| OQ-TC-18 | To ensure the final report proves which version of the software was used. | - The software version (e.g., v1.1.0) is clearly printed on the report. |
| OQ-TC-20 | To prevent the entry of logically impossible limits (e.g., High Limit < Low Limit). | - The system displays: "ERR-006: Configuration Error - High Limit cannot be lower than Low Limit." |
| OQ-TC-21 | To verify that audit logs match the local workstation system clock. | - The log timestamp matches the Windows clock. |
| OQ-TC-22 | To verify that the system identifies the Windows User account performing the actions. | - The "User" field exactly matches the currently logged-in Windows Username. |
| OQ-TC-25 | To ensure the system refuses to run if the audit trail file is deleted. If the history of the system's actions is missing, the system cannot be considered "validated" or "secure." Deleting the log file is a common way to hide unauthorized actions, so the system must prevent this. | - The application fails to launch the main processing interface. - The system automatically creates a new, empty `audit_trail.log` file. |